METERING REQUIREMENTS

[Insert SLD showing location of the metering facility. PCB, DS, Metering equipment, and the Transmission Customer should be seen in the SLD.]

METERING POINT LOCATION AND EQUIPMENT ARRANGEMENT

- The metering point between the Grid and the Transmission Customer shall be within 500 meters from the connection point. The connection point shall be determined in accordance to ERC Resolution 23 Series of 2016.

- The metering facility shall be located between the disconnect switch and the circuit breaker (see figures 1 and 2 for the typical arrangements).

Figure 1. Metering Facility at Customer Side

NGCP

NGCP

Grid

Grid

Figure 2. Metering Facility at NGCP Side

- The Voltage and Current Transformers shall be positioned relative to the direction of normal power flow in a manner that the Voltage Transformers do not pose as a load to the Current Transformers. Location of Lightning Arresters may vary depending on the connection point location.

- METERING FACILITY

- The metering circuit shall be Blondel’s Theorem compliant.

- The instrument transformers of the metering facility shall be used exclusively for revenue metering service.

- The following shall not be allowed:

  - Use of ‘totalizing’ and/or parallel connected current transformers (CT) for revenue metering service; and

  - Use of a single set of voltage transformers (VT) to serve more than one metering point.

- The metering facility shall comply with the requirements of the prevailing versions of the Philippine Grid Code, WESM Manual on Metering Standards and Procedures and relevant issuances of the Department of Energy (DOE) and Energy Regulatory Commission (ERC).

- The Grid metering facility shall consist of:

  - Instrument transformers and their mounting structures;

  - Surge arrester, if there is no other surge arrester at the Connection Point;

  - Revenue-class meters;

  - Data communication devices;

  - Meter security enclosure and conduits; and

  - Interconnecting cables, wires, and associated devices, i.e., test switches, etc.

- REQUIREMENTS FOR THE REVENUE METERING EQUIPMENT

Voltage Transformers (VT)

The VT shall be compliant to the prevailing versions IEC 61869-3 or IEEE C57.13 Standard, with the following qualifications:

- The Accuracy Class shall be in accordance with Table 2 or better. Proof of compliance shall be shown in the Routine Test Report;

- The total burden of the metering circuit, consisting of the burdens coming from all the connected devices and secondary cables shall be within the burden range of the VT in Table 2;

- The secondary voltage shall be such that the nominal voltage ratio is a whole number;

Refer to the attached Technical Specifications for the standard VT ratios. Strictly follow the recommended VTR to ensure spares provision by NGCP.

- The VT may be equipped with an additional secondary winding that shall be used exclusively for a redundant revenue metering circuit;

- A Type Test Report and Routine Test Report which document compliance to IEC 61869-3 or IEEE C57.13 Standard shall be on file with the Metering Service Provider (MSP); and

- Refer to the attached specifications of VT for the complete requirements.

Current Transformers (CT)

The CT shall be compliant to the prevailing versions of IEC 61869-2 or IEEE C57.13 Standard, with the following qualifications:

- The CT ratio to be used shall be such that the expected minimum and maximum operating currents fall within the range where the ratio and phase accuracies are certified in accordance with the applicable IEC or IEEE Standard. This requirement is applicable for measurement of energy delivered to and received from the Grid;

Refer to the attached Technical Specifications for the standard CT ratios. Strictly follow the recommended CTR to ensure spares provision by NGCP.

- The accuracy class shall be in accordance with Table 2 or better. Proof of compliance shall be shown in the Routine Test Report;

- The total burden of the metering circuit, consisting of the burdens coming from all the connected devices and secondary cables shall shall be within the burden range of the CT in Table 2 but not exceeding the limit specified in the prevailing version of the PGC (2.5VA as per PGC 2016);

- The CT may be equipped with an additional secondary core and the winding that shall be used exclusively for a redundant revenue metering circuit;

- A Type Test Report and Routine Test Report which document compliance to IEC 61869-2 or IEEE C57.13 Standard shall be on file with the MSP; and

- Refer to the attached technical specifications of CT for the complete requirements.

Table 2. IEC and IEEE Instrument Transformers

|  | Customer | Instrument Transformer | Metering Accuracy Class | Burden Designation | Rated Burden, VA (1) | Burden Range (2) |
| --- | --- | --- | --- | --- | --- | --- |
| IEEE | Generator | CT | 0.15 | E-0.2 | 5 | 1VA-100% |
|  |  | VT | 0.15 | Y | 75 | 0-100% |
|  | Load | CT | 0.3 | B-0.2 | 5 | 1VA-100% |
|  |  | VT | 0.3 | Y | 75 | 0-100% |
| IEC | Generator | CT | 0.2s | - | 5 | 1VA-100% |
|  |  | VT | 0.2 | - | 75 | 0-100% |
|  | Load | CT | 0.2 | - | 5 | 1VA-100% |
|  |  | VT | 0.2 | - | 75 | 0-100% |

Notes: (1) Maximum Rated Burden  (2) Percent of Rated Burden wherein the accuracy class is guaranteed