PROTECTION ARRANGEMENTS AND SETTINGS

LARGE GENERATOR / DISTRIBUTION UTILITY / DIRECTLY CONNECTED LOAD

- __(Transmission Customer)__

- GENERAL REQUIREMENTS

  - A circuit breaker fail protection at the connection point shall be provided by Generator and Load Customer for connection at 500 kV, 230 kV or 138 kV Grid.

  - The line protection to be connected in the connection point should be able to clear any fault along the line segment with the following fault clearing time as per Philippine Grid Code (PGC) 2016 Edition Section GPR 7.3.2.2.1:

- 85 ms for 500 kV;

- 100 ms for 230 kV and 138 kV; and

- 120 ms for less than 138 kV

    - If the fault persists after the required clearing time, NGCP will provide backup operation at the connection point.

- All Generation Companies shall submit the list and details of their protection system to the System Operator for approval prior to energization (GPR 7.4.1.2)

- The protection of Generating Units and Equipment and their connection to the Grid shall be designed, coordinated, and tested to achieve the desired level of speed, sensitivity, and selectivity in fault clearing and to minimize the impact of faults on the Grid (GPR 7.4.1.3).

- The Grid User shall submit to NGCP the protection scheme and settings of their installed equipment with corresponding test results

- The actual protection arrangement and settings shall be in accordance with the Network Protection Philosophy of NGCP

- The actual protection arrangement and settings shall be in compliance with the approved Facility Study

- The actual protection arrangement shall be in accordance with the standard protection scheme based on NGCP’s requirement for EVOSS

- The actual protection arrangement and settings should be in accordance with the common source of time synchronization so it would be aligned to the whole NGCP grid.

- The grid user shall timely provide relevant information and necessary data to NGCP during significant-events in preparation for Significant Incident Reporting and post-disturbance analysis (GO 6.3.3.9 and GO 6.3.4.7).

- Conventional, VRE Generating Facilities, Distribution Utilities, and Directly connected Loads shall be equipped with a data acquisition system, disturbance recorder and fault locator for monitoring and recording system performance and such equipment shall be remotely accessed by the System Operator for real-time fault data retrieval.

The minimum fault data requirement shall consist of but not limited to the following:

- Three (3) Phase voltages and four (4) currents including ground transient record of the lines connected to the grid.

- Three (3) Phase voltages and four (4) currents including ground transient record each at the primary and secondary side of the  transformers connected to the grid.

- Generator, unit transformer and transmission line protection operation and status indications

- Breaker status operation and indications

- If there are changes in the approved proposed protection design, the approved Transmission Service Agreement shall be subjected for revision.

- STANDARD PROTECTION SCHEME

# Table 1: Standard Tele-Protection Scheme for Grid Connected Generator and Load Customers using Single or Double Circuit Line for 115 kV and above

| # Protection |  | # Tele-Protection |
| --- | --- | --- |
| # NGCP SS | # Power Plant / Load |  |
| # Line Differential (87L) Main 1 | # Line Differential (87L) Main 1 | # *Fiber Optic via OPGW |
| # Line Differentail (87L) Main 2 | # Line Differential (87L) Main 2 | # *Fiber Optic via OPGW |

# Note: *Requires two (2) physically separate Fiber Optic links

# Table 2:  Standard Tele-Protection Scheme for Grid Connected Generator and Load Customers directly connected via 69 kV system

| # NGCP SS | # Power Plant / Load |
| --- | --- |
| # Directional Phase & Ground Overcurrent (67/67N) Main 1 | # Non-directional Phase & Ground Overcurrent (50/51, 50/51N) Main 1 |
| # Directional Phase & Ground Overcurrent (67/67N) Main 2 | # Non-directional Phase & Ground Overcurrent (50/51, 50/51N) Main 2 |

# Table 3: Standard Tele-Protection Scheme for Grid Connected Generator and Load Customers with Tap Connection along 69 kV line

| # NGCP SS | # Tapping Point | # Power Plant / Load |
| --- | --- | --- |
| # Directional Phase & Ground Overcurrent (67/67N) Main 1 | # Non-directional Phase & Ground Overcurrent (50/51, 50/51N) Main 1 | # Non-directional Phase & Ground Overcurrent (50/51, 50/51N) Main 1 |
| # Directional Phase & Ground Overcurrent (67/67N) Main 2 | # Non-directional Phase & Ground Overcurrent (50/51, 50/51N) Main 2 | # Non-directional Phase & Ground Overcurrent (50/51, 50/51N) Main 2 |

# The Main 1 and Main 2 protection listed in Tables 1 to 3 shall be of different manufacturers.

[Insert schematic diagram of ___.]

[Insert schematic diagram of ___.]

DIAGRAM OF ____